## SIDCT Results
Project | Route | Line Tag | Service | Material | Catalog | DN Governing [mm] | Governing Criterion | Velocity [m/s] | Pressure Drop [bar] | Head Loss [m] | Flow Depth Ratio | Slope Adequacy | Self Cleansing OK | Selected Schedule | Selected Wall [mm] | Checker Status | Governing Issue | Warnings | Dataset Missing | Out of Scope | Calculated At | Schema Version
SIDCT Project | Route A | L-001 | sanitary_drainage | PVC | PVC_EN1452 | 40 | fill_ratio | 0.616 | N/A | N/A | 0.595 | OK | Yes | PN10 | 3.7 | APPROVED | N/A | Check SN class for buried loading and local fire/acoustic requirements.; temperature and fire/acoustic requirements; PVC pressure rating requires temperature derating above 20 C; verify manufacturer table for final design.; PVC-U dataset is for water and drainage services only.; Do not use for compressed air, natural gas, vacuum or fire-water approval.; Temperature derating must be checked for final design above 20 °C.; PVC-U pressure thickness uses simplified public hoop-stress screening; verify manufacturer pressure/temperature derating for final design.; No user plastic derating dataset found for PVCU_EU. Add manufacturer data at D:\Onedrive\OneDrive - Tensor - Construção Civil Lda\Documentos\Paulo\AP\GitHub\iss-industrial-piping-dc\data\user_supplied\plastic_derating.yaml for final design.; PVC-U EN/ISO pressure pipe support span uses indicative short-term modulus E = 3 GPa; verify manufacturer support tables.; Factor sísmico padrão: 0.1g. Substituir por factor local conforme zonamento sísmico.; MÉTODO: Estimativa de Engenharia (modelo bi-apoiado estático). Para sistemas sujeitos a expansão térmica ou dinâmicas complexas, requer-se análise formal de tensões.; schedule_or_wall_received não fornecido — verificação de espessura parcial | N/A | N/A | N/A | N/A

## Line Inputs
Route | Project | Line Tag | Service | Project Profile | Jurisdiction | Fluid Name | P Oper Bar | T Oper C | P Design Bar | T Design C | Flow Rate | Flow Rate Basis | Line Length M | Elevation Delta M | Material | Dimensional Catalog | Design Code | Corrosion Allowance Mm | Allowable Pressure Drop Bar | Dn Received Mm | Schedule Or Wall Received | Slope Mm M | Vacuum Target Mbara | Operation Mode | Design Notes
Route A | SIDCT Project | L-001 | sanitary_drainage | glass_factory_industrial_eu | EU | sanitary_drainage | 6 | 20 | 10 | 40 | 0.5 | L/s | 10 | 0 | PVC | PVC_EN1452 | N/A | 1.5 | 0.5 | 40 | N/A | 15 | N/A | calculate_new | N/A

## Audit
Timestamp | Action | Line Tag | Message | Details
2026-05-04T11:17:56+00:00 | add_route |  | Route added: Route A | {"route_id": "93bd1989-d793-4d58-8262-e2df6680d882"}
2026-05-04T11:17:57+00:00 | calculate_line | L-001 | Line calculated: L-001 | {"status": "APPROVED"}

## Warnings
Route | Line Tag | Status | Warnings | Dataset Missing | Out Of Scope
Route A | L-001 | APPROVED | Check SN class for buried loading and local fire/acoustic requirements.; temperature and fire/acoustic requirements; PVC pressure rating requires temperature derating above 20 C; verify manufacturer table for final design.; PVC-U dataset is for water and drainage services only.; Do not use for compressed air, natural gas, vacuum or fire-water approval.; Temperature derating must be checked for final design above 20 °C.